{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":49,"n_cols":11,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ADEA-A"]
[]
[]
[]
[]
["","","","","","ADEA35A2VEB","ADEA50A2VEB","ADEA60A2VEB","ADEA71A2VEB","ADEA100A2VEB","ADEA125A2VEB"]
["Ventilator","Externer statischer Druck","","Hoch","Pa","150","150","150","150","150","150"]
["Kühlleistung","Gesamtleistung","","Nom.","kW","","","","","","14.00"]
["Heizleistung","Gesamtleistung","","Heizleistung-=-Gesamtleistung-=-Nom.-=-kW","kW","","","","","","13.50"]
["Gehäuse","Farbe","","","","Ohne Farbauftrag (galvanisiert)","Ohne Farbauftrag (galvanisiert)","Ohne Farbauftrag (galvanisiert)","Ohne Farbauftrag (galvanisiert)","Ohne Farbauftrag (galvanisiert)","Ohne Farbauftrag (galvanisiert)"]
["","Material","","","","Galvanisiertes Stahlblech_","Galvanisiertes Stahlblech_","Galvanisiertes Stahlblech_","Galvanisiertes Stahlblech_","Galvanisiertes Stahlblech_","Galvanisiertes Stahlblech_"]
["Abmessungen","Maßeinheit","","Höhe","mm","245","245","245","245","245","245"]
["","","","Breite","mm","700","700","1000","1000","1400","1400"]
["","","","Tiefe","mm","800","800","800","800","800","800"]
["Gewicht","Maßeinheit","","","kg","28","28","35","35","46","46"]
["Ventilator","Luftstromvolumen","Kühlen","Hoch","m³/min","15","15","18","18","29","34"]
["","","","Mittel","m³/min","12.5","12.5","15","15","26","29"]
["","","","Niedrig","m³/min","10.5","10.5","12.5","12.5","23","23.5"]
["","","Heizen","Hoch","m³/min","15","15","18","18","29","34"]
["","","","Mittel","m³/min","12.5","12.5","15","15","26","29"]
["","","","Niedrig","m³/min","10.5","10.5","12.5","12.5","23","23.5"]
["","Externer statischer Druck","","Nom.","Pa","30","30","30","30","40","50"]
["Schallleistungspegel","Kühlung","","","dB(A)","60","60","56","56","58","62"]
["Schalldruckpegel","Kühlen","","Hoch","dB(A)","35","35","30","30","34","37"]
["","","","Schalldruckpegel-=-Kühlen-=-Mittel-=-dB(A)","dB(A)","32","32","28","28","32","35"]
["","","","Niedrig","dB(A)","29","29","25","25","30","32"]
["","Heizen","","Hoch","dB(A)","37","37","31","31","36","38"]
["","","","Schalldruckpegel-=-Heizen-=-Mittel-=-dB(A)","dB(A)","34","34","28","28","33","35"]
["","","","Niedrig","dB(A)","29","29","25","25","30","32"]
["Rohrleitungsanschlüsse","Flüssigkeit","","AD","mm","6.35","6.35","6.35","9.52","9.52","9.52"]
["","Gas","","AD","mm","9.52","12.7","12.7","15.9","15.9","15.9"]
["","Ableitung","","","","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)"]
["Entleerungshöhe","mm","","","","625","625","625","625","625","625"]
["Regelungssysteme","Infrarot-Fernbedienung","","","","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66"]
["","Verkabelte Fernbedienung","","","","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52"]
["Standardzubehör","Installation manual","","","","1","1","1","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8","8","8","8"]
["","Operation manual","","","","1","1","1","1","1","1"]
["","Clamps","","","","4","4","4","4","4","4"]
["","Drain hose","","","","1","1","1","1","1","1"]
["","Insulation for fitting","","","","2","2","2","2","2","2"]
["","Metal clamp for drain hose","","","","1","1","1","1","1","1"]
["","Screws","","","","40","40","40","40","40","40"]
["","Sealing pads","","","","5","5","5","5","5","5"]
["Stromversorgung","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Frequenz","","","Hz","50","50","50","50","50","50"]
["","Spannung","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Hinweise","","","","","","","","(1) - Der Schallleistungspegel ist ein Absolutwert, den eine Geräuschquelle abgibt.","(1) - Der Schallleistungspegel ist ein Absolutwert, den eine Geräuschquelle abgibt.","(1) - Der Schallleistungspegel ist ein Absolutwert, den eine Geräuschquelle abgibt."]
["","","","","","","","","(2) - Siehe separate Zeichnung für die elektrischen Daten","(2) - Siehe separate Zeichnung für die elektrischen Daten","(2) - Siehe separate Zeichnung für die elektrischen Daten"]