{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":8,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DW1P-H"]
[]
[]
[]
[]
["","","","","","EWAA011DAW1P-H-","EWAA014DAW1P-H-","EWAA016DAW1P-H-"]
["Schalldruckpegel","Kühlen","","Nom.","dBA","47.7","50.8","51.0"]
["Hydraulikkomponenten","Ausdehnungsgefäß","","Volumen","l","8","8","8"]
["Betriebsbereich","Luftseite","Kühlen","Min.","°C Trockenkugel","10","10","10"]
["","","","Max.","°C Trockenkugel","43","43","43"]
["","Wasserseite","Kühlen","Max.","°C Trockenkugel","22","22","22"]
["","","","Min.","°C Trockenkugel","5","5","5"]
["Kältemittelfüllmenge","pro Kreislauf","","","kg","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6"]
["Verdichter","Typ","","","","Vollhermetischer Swing-Inverter-Verdichter","Vollhermetischer Swing-Inverter-Verdichter","Vollhermetischer Swing-Inverter-Verdichter"]
["","Starting method","","","","Invertergeregelt","Invertergeregelt","Invertergeregelt"]
["","Anzahl_","","","","1","1","1"]
["Luftwärmetauscher","Typ","","","","Hochleistungs-Rippenrohrtyp mit integriertem Unterkühler","Hochleistungs-Rippenrohrtyp mit integriertem Unterkühler","Hochleistungs-Rippenrohrtyp mit integriertem Unterkühler"]
["Gewicht","Maßeinheit","","","kg","147","147","147"]
["EER","","","","","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Kältemittel","GWP","","","","675.0","675.0","675.0"]
["","Typ","","","","R-32","R-32","R-32"]
["","Kreisläufe","","Anzahl","","1","1","1"]
["","Regelung","","","","Elektronisches Expansionsventil","Elektronisches Expansionsventil","Elektronisches Expansionsventil"]
["Ventilatormotor","Drehzahl","Kühlen","Nom.","U/min","550","650","650"]
["Kühlleistung","Nom.","","","kW","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Wasserwärmetauscher","Wasservolumen","","","l","2","2","2"]
["","Mindestwasservolumen im System","","","l","20 (6)","20 (6)","20 (6)"]
["","Typ","","","","Platten-Wärmetauscher","Platten-Wärmetauscher","Platten-Wärmetauscher"]
["Leistungsaufnahme","Kühlen","","Nom.","kW","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["Schallleistungspegel","Kühlen","","Nom.","dBA","67.0","69.0","69.0"]
["Abmessungen","Maßeinheit","","Breite","mm","1,380","1,380","1,380"]
["","","","Tiefe","mm","460","460","460"]
["","","","Höhe","mm","870","870","870"]
["Leistungsregelung","Verfahren","","","","Variabel (Inverter)","Variabel (Inverter)","Variabel (Inverter)"]
["Ventilator","Luftstromvolumen","Kühlen","Nom.","m³/min","70","85","85"]
["Verdichter","Starting method","","","","Inverter","Inverter","Inverter"]
["Power supply","Phase","","","","3~","3~","3~"]
["","Frequenz","","","Hz","50","50","50"]
["","Bezeichnung","","","","W1","W1","W1"]
["","Spannung","","","V","400","400","400"]
["Hinweise","","","","","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK"]
["","","","","","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK"]
["","","","","","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825","(5) - Entsprechend EN 14825"]
["","","","","","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung."]
["","","","","","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung."]