{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":12,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWH-J-SS"]
[]
[]
[]
[]
["","","","","","EWWH090J-SS","EWWH110J-SS","EWWH120J-SS","EWWH130J-SS","EWWH150J-SS","EWWH180J-SS","EWWH200J-SS"]
["Kühlleistung","Nom.","","","kW","88.77","107.1","115.1","133.5","150.1","181.6","200.6"]
["Leistungsregelung","Verfahren","","","","Stufenlos","Stufenlos","Stufenlos","Stufenlos","Stufenlos","Stufenlos","Stufenlos"]
["","Mindestleistung","","","%","25","25","25","25","25","25","25"]
["Leistungsaufnahme","Kühlen","","Nom.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.59"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Abmessungen","Maßeinheit","","Tiefe","mm","2684","2684","2684","2684","2684","2684","2684"]
["","","","Höhe","mm","1020","1020","1020","1020","1020","1020","1020"]
["","","","Breite","mm","913","913","913","913","913","913","913"]
["Gewicht","Betriebsgewicht","","","kg","1211","1276","1378","1415","1473","1663","1675"]
["","Maßeinheit","","","kg","1177","1233","1334","1366","1416","1600","1607"]
["Gehäuse","Farbe","","","","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß","Elfenbeinweiß"]
["","Material","","","","Galvanisiertes Stahlblech","Galvanisiertes Stahlblech","Galvanisiertes Stahlblech","Galvanisiertes Stahlblech","Galvanisiertes Stahlblech","Galvanisiertes Stahlblech","Galvanisiertes Stahlblech"]
["Wasserwärmetauscher - Verdampfer","Typ","","","","Platten-Wärmetauscher","Platten-Wärmetauscher","Platten-Wärmetauscher","Platten-Wärmetauscher","Platten-Wärmetauscher","Platten-Wärmetauscher","Platten-Wärmetauscher"]
["","Wasservolumen","","","l","14","18","14","17","20","26","26"]
["Wasserwärmetauscher – Verdampfer","Wasserdruckabfall","Kühlen","Nom.","kPa","10.7","10.9","19.3","19.3","17.8","16.8","20.1"]
["Verdichter","Anzahl","","","","1","1","1","1","1","1","1"]
["","Typ","","","","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter","Monoschraubenverdichter"]
["","Startmethode","","","","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck","Ypsilon-Dreieck"]
["Betriebsbereich","Wasserseite","Verdampfer","Betriebsbereich-=-Wasserseite-=-Verdampfer-=-Min.-=-°C TK","°C TK","-5","-5","-5","-5","-5","-5","-5"]
["","","","Betriebsbereich-=-Wasserseite-=-Verdampfer-=-Max.-=-°C TK","°C TK","25","25","25","25","25","25","25"]
["Schallleistungspegel","Kühlen","","Nom.","dB(A)","95","95","95","95","95","95","95"]
["Schalldruckpegel","Kühlen","","Nom.","dB(A)","79","79","79","79","79","79","79"]
["Kältemittel","Typ","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["","GWP","","","","1.4","1.4","1.4","1.4","1.4","1.4","1.4"]
["","Füllmenge","","","kg","18","35","34","37","37","38","38"]
["","Kreisläufe","","Anzahl","","1","1","1","1","1","1","1"]
["Rohrleitungsanschlüsse","Wassereinlass / -auslass Verdampfer (AD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["Energieeffizienzbereich","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Stromversorgung","Phase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Frequenz","","","Hz","50","50","50","50","50","50","50"]
["","Spannung","","","V","400","400","400","400","400","400","400"]
["","Spannungsbereich","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10"]
["Gerät","Anlaufstrom","","Max.","A","153","153","197","197","197","290","290"]
["","Betriebsstrom","Kühlung","Nom.","A","39","44","55","60","65","76","84"]
["","","","Max.","A","75","90","100","114","143","158","178"]
["","Max. Gerätestrom für Kabelgrößen","","","A","83","100","112","127","159","176","198"]
["Hinweise","","","","","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK","(1) - Kühlen: EW 12 °C; AW 7 °C; Umgebungsbedingungen: 35 °C TK"]
["","","","","","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK","(2) - Kühlen: EW 23 °C; AW 18 °C; Umgebungsbedingungen: 35 °C TK"]
["","","","","","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Bedingung: Ta TK/FK 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Bedingung: Ta TK/FK 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Entsprechend EN14825","(5) - Entsprechend EN14825","(5) - Entsprechend EN14825","(5) - Entsprechend EN14825","(5) - Entsprechend EN14825","(5) - Entsprechend EN14825","(5) - Entsprechend EN14825"]
["","","","","","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung.","(6) - Von der Betriebsart abhängig, siehe Installationsanleitung."]
["","","","","","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung.","(7) - Weitere Informationen in der Betriebsbereichszeichnung."]