{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":28,"n_cols":16,"rows_kept":28,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-VZSS"]
[]
[]
[]
[]
["","","","","EWWS600VZSSA1","EWWS700VZSSA1","EWWS740VZSSA1","EWWS880VZSSA1","EWWSC10VZSSA1","EWWSC12VZSSA2","EWWSC13VZSSA2","EWWSC14VZSSA2","EWWSC15VZSSA2","EWWSC17VZSSA2","EWWSC18VZSSA2","EWWSC20VZSSA2"]
["Kühlleistung","Nom.","","kW","600","694","744","880","1,020","1,149","1,263","1,352","1,515","1,690","1,832","2,013"]
["Leistungsregelung","Verfahren","","","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel","Variabel"]
["","Mindestleistung","","%","20","20","20","20","20","10","10","10","10","10","10","10"]
["Leistungsaufnahme","Kühlen","Nom.","kW","120.1","143.3","154.7","175.2","212.7","251.8","273.9","301","343","367.4","413.5","437.2"]
["EER","","","","4.99","4.84","4.81","5.02","4.8","4.56","4.61","4.49","4.42","4.6","4.43","4.61"]
["ESEER","","","","0","0","0","0","0","0","0","0","0","0","0","0"]
["Abmessungen","Maßeinheit","Tiefe","mm","3,722","3,750","3,750","3,690","3,822","4,792","4,792","4,792","4,792","4,508","4,508","4,750"]
["","","Höhe","mm","2,123","2,123","2,123","2,292","2,487","2,296","2,296","2,296","2,296","2,350","2,338","2,498"]
["","","Breite","mm","1,178","1,179","1,179","1,233","1,303","1,484","1,487","1,487","1,484","1,580","1,627","1,753"]
["Gewicht","Maßeinheit","","kg","2,892","2,928","2,941","3,451","4,237","5,570","5,790","5,820","6,220","6,890","7,260","8,260"]
["","Betriebsgewicht","","kg","2,977","3,033","3,053","3,611","4,488","5,980","6,220","6,290","6,690","7,480","7,830","9,070"]
["Wasserwärmetauscher - Verdampfer","Typ","","","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer"]
["","Wasservolumen","","l","88","88","96","134","156","230","230","270","270","320","320","380"]
["Wasserwärmetauscher - Kondensator","Typ","","","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer","Überfluteter Bündelrohrverdampfer"]
["Verdichter","Type","","","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter","Invertergeregelter Monoschraubenverdichter"]
["","Anzahl_","","","1","1","1","1","1","2","2","2","2","2","2","2"]
["Schallleistungspegel","Kühlen","Nom.","dBA","101","105","105","105","107","106","106","107","107","108","108","110"]
["Schalldruckpegel","Kühlen","Nom.","dBA","82","86","86","86","88","87","87","88","88","89","89","90"]
["Kältemittel","Typ","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","Füllmenge","","kg","100","110","110","170","180","250","260","270","290","295","320","350"]
["","Kreisläufe","Anzahl","","1","1","1","1","1","2","2","2","2","2","2","2"]
["","GWP","","","631","631","631","631","631","631","631","631","631","631","631","631"]